SECTION 28 15 21 ACCESS CONTROL

TELEPHONE ENTRY SYSTEMS

DoorKing 1800 Series

Display hidden notes.  (Don’t know how?  Click Here)

This specification is based on products from DoorKing, Inc.

120 S. Glasgow Ave.

Inglewood, CA  90301

Tel:  800-826-7493

Fax:  310-641-1586

Email:	info@doorking.com

Web:		www.doorking.com

DoorKing (DKS) was founded in 1948.  The company is one of the largest and oldest manufacturers of access control and vehicular gate operator products in the United States and offers a full line of residential, commercial and industrial products to meet the needs of Architects, Designers, Engineers and Specifiers in almost any design or conceptual plan.  DoorKing is a registered provider of the American Institute of Architects continuing education system.  For learning objectives and to schedule a Lunch & Learn, please send a request to awright@doorking.com.  For a complete library of CSI format 3-part specs, CAD and BIM product renderings, visit doorking.com/architects-specifiers.

PART 1 GENERAL

1.1	WORK INCLUDED

A.	Furnish and install a complete microprocessor controlled "full-duplex" circuitry voice communication, telephone entry system as described herein and shown on the plans.  The system shall include all necessary boards, power supplies, keypads, loudspeakers, special mounting boxes, cable, connectors, and accessories for a complete operational communication system.

B.	Scope of work shall include communication and access control for up to 600 users.

1.2	CONTRACT DOCUMENTS

A.	All equipment and work specified in this section shall comply, with all the General Conditions of the specifications, contract documents, and drawings as indicated.

1.3	RELATED WORK

A.	Contractor shall coordinate all work with other contractors and trades where necessary.

B.	All necessary conduit, raceways, pull boxes, standard boxes, (and special boxes provided by intercom manufacturer), shall be installed by the electrical contractor.

C.	Installation of the communication/access systems shall be coordinated with the installation of other related systems.

1.4	QUALITY ASSURANCE

A.	Installation shall comply with all applicable codes.

B.	All equipment shall be new, in current production, and the standard products of a manufacturer of telephone entry system equipment.

C.	Manufacturer shall guarantee availability of parts, for a minimum of 7-years from date of shipment.

D.	If required, manufacturer shall be able to demonstrate features, functions and operating characteristics.

E.	System shall be installed by a factory authorized contractor, with technicians specifically trained in this system.

F.	On-site maintenance and repair service shall be available locally and within 4-hours, of notification for emergency condition.

G.	System shall interface with other DoorKing systems to allow remote PC programming.

1.5	REFERENCE STANDARDS

A.	Underwriter Laboratories Inc. (UL), UL 294

B.	Telephone Entry System shall be tested for compliance to UL 294 and shall be LISTED by a Nationally Recognized Testing Laboratory (NRTL).

C.	Federal Communications Commission (FCC).

D.	Department of Commerce (DOC) (CAN).

1.6	SUBMITTALS

A.	Provisions:  Comply with Section 01300 SUBMITTALS.

B.	Shall include an equipment list, and data sheet, system description and block diagrams on equipment to be finished.

C.	Shall include all data necessary to evaluate design, quality, and configuration of proposed equipment and system(s).

1.7 	WARRANTY

A.	Systems shall include a factory warranty that equipment is free from defects in design, material, manufacturing and operation.

B.	Factory warranty period shall be for two (2) years parts and workmanship; 24-months from date of shipment. Manufacturer shall not be responsible for improper use, handling, or installation of the product.

C.	Installing communications contractor shall guarantee the equipment, wire, cable, and installation for 12-months from date of acceptance.

PART 2 - PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

A.	The system as described herein, is based on the 1800 Series Telephone Entry system manufactured by DoorKing, Inc., Inglewood, California. The 1800 series system specified meets requirements of the specifications and shall be considered as the acceptable Base Bid.

B.	Substitutions must meet requirements of Prior Approval, as outlined in the contract documents.  Substitutions that meet Prior Approval requirements must be listed as alternates by addendum, and shall be shown separately on the bid forms.  Consideration will be based on ability to comply with all aspects of the specifications, the desired functional operation, quality, reliability, design, size, and appearance of the equipment, and the support capabilities of the manufacturer.

2.2	SYSTEM DESCRIPTION

A.	The telephone entry system shall provide "full duplex," (hands-free at guest end) voice communication from the entry location to the resident telephone.  Half duplex or simplex type communication will not be allowed.

B. The system shall be capable of storing up to 600 user phone numbers (exception, model 1802-EPD stores 100 phone numbers).

C.	The system shall be capable of independently controlling a main entry access point plus an additional (non-communicating) access point.

D.	Directory codes shall be programmable from one (1) to four (4) digits.

E.	Tone-open numbers to grant guest access shall be programmable.  Additional tone open number commands shall include hold-open, close and hold-open one hour and then close.

F.	A built-in time clock shall provide hold-open time zones and entry code time zones.

G.	Two special inputs shall be available and programmable to allow activation of a system relay or to automatically call a preprogrammed phone number.

H.	The system shall be capable of sending DTMF tones after a call from the system is connected.

I.	The telephone entry system shall be prewired for installation of a postal lock (exception model 1808).

J.	A provision for postal lock input shall allow and record entries by post office personnel.

K.	Cabinet

1.	Cabinet is constructed from 16-gauge steel and is lockable, gasketed, NEMA 4 rated enclosure.

2.	The telephone entry system shall be of hands-free design.

3.	The speaker holes shall be offset to protect the speaker from vandalism.

4.	The system shall utilize metal keypad and metal push buttons.

5.	The control board shall be mounted to the rear of the system enclosure to protect it from vandalism.

6.	The stainless steel faceplate shall be reinforced with a galvanized steel sub-plate. Faceplate shall be non-magnetic steel alloy #304 or #316 as per ASTM A167, A176, A408, and A484.

2.3	EQUIPMENT

Select access system model. Delete four of the following five items (A-B-C-D-E).

A.	Model 1802 Telephone Entry System.

1.	600 phone numbers maximum, no directory.

2.	Mounting

Delete one of the following two items (i-ii).

i.	Surface Mount

6 1/2 inches wide, 12 inches high, 5 inches deep.

ii.	Flush Mount

8 3/8 inches wide, 14 inches high, 3 1/4 inches deep.

B.	Model 1802-EPD Telephone Entry System.

1.	100 phone numbers maximum, built-in LCD scrolling directory (100 names maximum).

2.	A-Z scroll buttons; CALL button.

3.	Mounting

Delete one of the following two items (i-ii).

i.	Surface Mount

6 1/2 inches wide, 12 inches high, 5 inches deep.

ii.	Flush Mount

8 3/8 inches wide, 14 inches high, 3 1/4 inches deep.

C.	Model 1803 Telephone Entry.

1.	600 phone numbers maximum, no directory.

2.	Mounting

Delete one of the following two items (i-ii).

i.	Surface Mount

11 1/4 inches wide, 13 inches high, 4 1/2 inches deep.

ii.	Flush Mount

12 inches wide, 13 1/4 inches high, 3 1/4 inches deep.

D.	Model 1808 Telephone Entry System.

1.	600 phone numbers maximum.

11 inches wide, 7 1/2 inches high, 6 1/2 inches deep.

Delete one of the following two items (i, ii).

i.	Surface Mount, No Directory

ii.	Surface Mount, Small Directory (10-12 names maximum).

E.	Model 1810 Telephone Entry System.

1.	600 phone numbers maximum, built-in lighted paper directory (100 names maximum).

2.	Mounting

Delete one of the following two items (i-ii).

i.	Surface Mount

11 1/4 inches wide, 13 inches high, 4 3/4 inches deep.

ii.	Flush Mount

12 inches wide, 13 1/4 inches high, 3 1/4 inches deep.

2.4 	OPTIONS

The following paragraphs are optional items.  Delete if not required.

A. Mounting kits.

Mounting kits simplify installation.  The manufacturer recommends the use of the flush mounting kit (p/n 1814-165) whenever the flush mount design is specified.  Does not apply to 1802 or 1802-EPD flush mount models.

1.	Surface mount recess kit (p/n 1803-150).

Use with surface mount 1803 and 1810 systems and 1710 directory only.

2.	Flush mount kit (p/n 1814-165).

Use with flush mount 1803 and 1810 systems and 1710 directory only.

B.	Add-On Directories.

Add-on directories are used to display the resident list so visitors know which code to use to contact them via the entry system. Add-on directories can be used with 1802, 1803 and 1810 systems.

1.	20-name directory – 1/4 inch name slots (p/n 1701-080).

2.	60-name directory – 1/4 inch name slots (p/n 1702-080).

3.	Lighted paper directory, surface mount, approximately 150 names (p/n 1710-080).

4.	Lighted paper directory, flush mount, approximately 150 names (p/n 1710-081).

C.	LED Light Kit (p/n 1720-080).

LED light kits provide additional lighting and can be used with the surface mount 1803, 1808 and 1810 systems only.

D.	Connection options

One (1) of the following three options is required.

1.	VoIP requires DoorKing P/N 1815-578 (VoIP subscription required).

2.	Cellular requires DoorKing P/N 1800-080 (cellular subscription 	required).

3.	POTS (Plain Old Telephone Service).

NOTE to specifier: Because of changes being made to the PSTN (Public 	Switched Telephone Network), DoorKing does not recommend and cannot 	guarantee programming of the system via a POTS line and modem any 	longer.

PART 3 - EXECUTION

3.1	INSTALLATION

A.	Should be installed by qualified technicians who have been factory trained.

B. Wiring shall be uniform and in accordance with national electric codes and manufacturers instructions.

C.	Conform to the manufacturers written requirements for installation. Systems are available for the following types of installation.

1.	Surface or Flush mounting (exception – 1808 is surface mount only).

2.	Flush mounted with the use of a flush kit (p/n 1814/165).

3.	Recess mounted with the use of a recess kit (p/n 1803-150).

4.	Post mounted using a heavy -duty gooseneck mounting post.

D. Equipment shall be firmly secured, plumb, and level.

E.	All splices shall be in easily accessible junction boxes or on terminal boards.

F.	All cable runs at the main control cabinets, in all auxiliary cabinets and at all phone blocks shall be tagged and identified.

G.	Coordinate all work with other effected trades and contractors.

H.	Fastenings:

1.	Fasten on gypsum board wall surfaces with screws into wood or metal blocking, or with bolts or molly anchors, not less than 1/4" diameter.  Screwing into gypsum board or plaster with plugs will not be acceptable.

2.	Fasten into concrete or masonry with self-drilling masonry anchors Phillips Redhead, Bulldog or Rawl Sabertooth.

3.2	SYSTEM INITIALIZING AND PROGRAMMING

A.	System shall include all instructions necessary for system configuration.

B.	System shall be turned on and adjustment made to meet requirements of specifications and on-site conditions.

C.	System shall be programmed to function as specified.

D.	Directory numbers, feature codes, and special programming shall be documented, printed and made available to all owners.

3.3	SYSTEM TEST PROCEDURES

A.	System shall be completely tested to assure that the exchange and all components, stations, speakers, and accessories are hooked-up and in working order.

B.	System shall be pre-tested by contractor and certified to function in accordance with plans and specifications.

C.	System shall be tested in presence of owner's representative.

3.4	OWNER INSTRUCTIONS

A.	Installation contractor shall conduct up to (4) hours of instruction in use and operation of the system to designated owner representatives, within (30) days of acceptance.

B.	Installation contractor shall conduct up to (4) hours of technical training, in programming, troubleshooting, and service of the system, to designated owner representatives within (90) days of system acceptance.

3.6	MANUALS AND DRAWINGS

A.	Contractor shall provide owner with (2) copies of standard factory prepared operation, installation and maintenance manuals.  Manuals shall include typical wiring diagrams.

B.	Contractor shall provide owner with (2) copies of any risers, layouts, and special wiring diagrams showing any changes to standard drawings, if required on project.

END OF SECTION